CENTRAL BOARD OF SECONDARY EDUCATION 

REGIONAL OFFICE

35-B, CIVIL STATION, M. G. MARG, CIVIL LINES,
 ALLAHABAD

TENDER NOTICE


Sealed tenders are invited on behalf of the Secretary, C.B.S.E., for the following works under Two Bid System :-

	Sl.

No.
	Scope of Work
	Location
	EMD
 #
	Essential qualification

	1.
	24 hrs O & M of Wet riser system & maint of Fire Detection / Alarm system.


	C.B.S.E., Regional Office Bldg, 35B, M.G. Marg, Civil Lines, Allahabad 
	Rs. 20,000/-


	1.  Should have executed atleast two similar works of value of Rs 1.8 Lac or more in multi story bldg.of  Govt./ Public Sector undertaking/ reputed organisations..



   # EMD is payable in form of BD/DD (Issued by Nationalised Bank Only) in favour of the Secretary CBSE, payable at Allahabad.  Tender can be purchased from the Cashier, CBSE, Regional Office, Allahabad against payment of Rs. 500/- on all working days between 10:00 a.m. to 1:00 p.m. upto 23 March 2012.  Last date for submission of tender is 26 March 2012 upto 1:00 p.m.

   Tender is to be submitted in the prescribed format in Two Bid System; Technical & Financial Bids be placed in two separate envelopes and both envelopes be kept in another bigger envelope duly sealed and superscribed “TENDER FOR FIRE FIGHTING WORK”.  The EMD and all requisite documents must be attached with the Technical-Bid and the Financial Bid should contain rates only.  Tenders duly filled in must be put in the tender box paced at Reception Counter, Regional Office Building upto 1:00 p.m. on or before 26 March 2012.  The technical Bids shall be opened on the same day at 3:00 p.m. in the presence of the tenderers.  Financial-Bids of qualified tenderers in the Technical-Bids will be opened later; the date & time for opening the Financial-Bids will be intimated.  Incomplete and conditional tenders shall be summarily rejected. 

   The Secretary, CBSE reserves the right to reject any or all the tenders without assigning any reason.









REGIONAL OFFICER

      Cost of form : Rs. 500/- (Non-refundable)                               Form No : _______

CENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE

35-B, CIVIL STATION, CIVIL LINES, M. G. MARG, ALLAHABAD

Ph.: 0532-2407970,2408971,2407972, Fax : 0532-2408977

PART-A Technical-Bid

                              Last date for receipt of tender : 26 March 2012 upto 01.00 p.m.
Name of work
: 24 hrs Operation & Maintenance of the Fire Fighting installation, 


   
  Wet riser; Fire Detection & Alarm System .  
Locations

: R.O. Bldg, 35-B, Civil Station, M.G. Marg, Civil Lines, Allahabad 
1.    Credentials of tenderer
1.1  Name of the agency:
             ________________________________________




  
1.2  Office Address and
  
  
       Tel. Nos.    


  ________________________________________ 

1.3  Electrical Licence from  
       Director Electrical Safety
       Govt. of U.P. Lucknow/Regd. with  Engg. govt. Organization.
       (with documentary evidence)
  ________________________________________
1.4  E.P.F A/c No.

       With latest challan 

  ________________________________________
1.5  PAN No.


  
      (with documentary evidence)
  ________________________________________
1.6  Sale Tax Regd. Certificate:  
       (with documentary evidence)
  ________________________________________
1.7  Service Tax Regd. Certificate
 
       (with documentary evidence)
  ________________________________________
2.    Annual turnover (last three years)  

	Sl. No
	Year
	Turn Over

	1.

	
	

	2.

	
	

	3.

	
	


-2-
3.1 Contracts executed corresponding to the NIT (To be supported with  documentary evidence) :
	S. No.
	Year
	Name of the organization
	Cost of the work (Executed)
	Officer Concd. in the organization with T. No.
	       Period



	
	
	
	
	
	From
	To

	1.

	
	
	
	
	
	

	2.

	
	
	
	
	
	

	3.

	
	
	
	
	
	


 3.2. Present assignment in hand corresponding to NIT for 24 hrs Operation &        Maintenance of the Fire Fighting installation, Wet rise  & Fire Detection / Alarm  System.

4.   Earnest Money of Rs. 20,000/- in favour of the “Secretary, CBSE, Allahabad”         has been deposited vide _____________________D/DD No. _______________dated _____________.
5.    Copy of the supporting documents in r/o information at Serial No. 1 to 3.1 above   & EMD must be enclosed.
6.    Declaration : All terms & conditions as mentioned in the Tender Documents are   acceptable to me/us.
     (Signature of the Tenderer)__________________
   Name & Address of Tenderer with seal__________________
__________________
Tel./Mobile No. ________________ 
Place : __________________
Date : ___________________ 

-3-
LIST OF ENCLOSURES
1. E.M.D. OF Rs. 20,000/- in the form of BD/DD No ___________________ dated 
____________ of Bank _______________________ (attached with technical bid only)

2.
List of clients.

3.
Performance certificate of last three works duly attested.

4.
Electrical licence from the Office of Director Electrical Safety, Govt of U.P. 
Lucknow/Regd. In Engg. Govt. Organisation
5.
The organizational set up including technical infrastructure.

6.
Analysis of rates.

7.
Any other documents.








      (Signature of the Tenderer)








With complete address and seal

Dated :  ___________

-4-
CENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE

35-B, CIVIL STATION, M.G. MARG, CIVIL LINES

ALLAHABAD

General Instructions to Tenderers

The tenderers are requested to note that non compliance of the following instruction is liable to render them non bona fide.

1.
The tenderers should read carefully the tender paper and examine general 
instruction, specifications, schedule of quantities etc.and for proper assessment 
of work may visit the site.
2.
The tenderers are required to check the number of the pages and if any is 
found missing or in duplicate, or the figure or writing indistinct the same be 
reflected with legible one.

3.
The tenderers should fill in all the relevant blanks line and put their signature 
on the relevant places as shown in the tender document.
4.
(a)  The tenderer shall quote his rates in figures as well as in words against 
relevant column and the same shall be duly attested.
(b)    No cutting/overwriting and use of whitener is permitted in Technical-Bid as well as Price-Bid.
(c)   Each page of the schedule of quantities and the Central Summary is to be signed by the tenderer.
5.
Tender marked original duly filled in and accompanied with earnest money as 
specified must be in sealed envelope submitted to the Regional Officer, CBSE, 
Regional Office, 35-B, M.G. Marg, Civil Lines, Allahabad on or before 1300 hrs 
on 26 March 2012.  The Technical-Bid will be opened on 26 March 2012 at 
1500 hrs in 
presence of tenderers or their accredited representative who 
desire to attend. 

6.
The tenderers are requested to put their firm’s endorsement on each page of 
the tender document as token of perusal.

7.
No alternations or addition should be made by the tenderers to the text of the 
schedule of these tender pages.  Violation of this instruction will lead rejection 
of the tender at the discretion of the Tender Inviting Authority.

8.
The tenderer who proposes any alterations to any of the condition laid down or 
proposes any other conditions of any description what-so-ever is liable to be 
rejected.

9.
No liability what-so-ever will be admitted nor any claim be allowed in respect 
of errors in the filled in tender documents due to mistake in the Price-Bid 
(Schedule of 
Quantities) which should have been rectified in the manner 
described above.
10.
Earnest Money accompanying the tender will be accepted only in the form of 
Demand Draft drawn in favour of the Secretary, CBSE payable at Allahabad.
11.
Earnest Money Deposit in the form of en-cashable cheque or Bank or Insurance 
Guarantee or Fixed Deposit Receipt will not be accepted.
12.
Tenderers should note that their tenders would remain open for consideration for a 
minimum period of THREE MONTHS from the date fixed for the receipt of tenders.
-5-
13.
The Tender Inviting Authority reserves the right to accept or to reject any or all 
tenders at its discretion without assigning any reasons thereof.  The Tender Inviting 
Authority does not bind to accept the lowest tender.




     (Signature of the Tenderer)_____________________
   Name & Address of Tenderer with seal_____________________
______________________
-6-
CENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE

35-B, CIVIL STATION, M.G. MARG, CIVIL LINES

ALLAHABAD


I hereby affirm that I have read all the instructions, terms & conditions before submission of the schedule of work and are acceptable to me.

     (Signature of the Tenderer)______________________
   Name & Address of Tenderer with seal______________________
​​______________________
Tel./Mobile No.:  _________________

Date    :  ____________

Place
:  _____________

-7-
CENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE

35-B, CIVIL STATION, M.G. MARG, CIVIL LINES

ALLAHABAD

1.  Credentials of tenderers.


1.1
Name of the Agency
:  ______________________________


1.2
Office address and tel. nos : __________________________


1.3
License No. & Registration details with documentary  evidence -  Annexure 1


1.4
P.F. A/C No. with documentary evidence


       -  Annexure 2

1.5
PAN No. with documentary evidence

       
 
       -  Annexure 3


1.6
Service Tax Regd. Certificate supported with 

       -  Annexure 4


Documentary evidence 

Condition of contract for Annual Maintenance & Operation of Fire Fighting and 
Fire Alarm System installed at CBSE, Regional Office Building, Allahabad.

2.      General.


      (a)
The contract is with a view to keep the entire fire fighting installation like     

down comer / wet-riser, fire pumps, fire panels, heat/smoke detection system in 

good serviceable condition to ensure their proper and effective functioning.  

The contract include the manning of above installation round the clock for   

CBSE, RO Bldg.  at Allahabad, so that the person on duty will keep a constant 

watch on fire pump, panel, hydrant etc. and shall operate the system promptly 

in case of any fire /emergency.


     (b)
The contractor for above work should be preferably qualified in fire safety and 

fire fighting equipments from Fire Engineering College  or they have the past 

experience  of erecting/maintenance of various type fire fighting installation.

.  
     (c)
The tender shall be valid for acceptance for a period of three months from 

the last date of receipt of tenders.  

     (d)
Maintenance Regulation.

(i) The contractor shall ensure that operation and maintenance of Fire-Installation is done as per the rules and regulations of Chief Fire Officer Allahabad and the parameters of NBC. The contractor shall strictly follow the instruction (either in writing or oral) time to time issued to them by the Regional Officer of his authorised representative.

-8-
(ii) The contractor or his authorised representative should be available as and when required to take instruction on fire extinguishing and fire fighting matters regarding maintenance and operation.

(e)
The scope of work, terms & conditions are as under :-

(i) Providing qualified and trained staff to operate and maintain the system round the clock.

(ii) Maintenance and operation of :-




(aa)
Down comer.




(ab)
Fire pump including periodical maintenance as per               



recommendation of fire pump manufacturer.





(ac)
Operation of each hydrants periodically (min 3 hydrants per 



week), de rolling the hose reels drying in same and 
putting back 



in the yard hydrant polishing (Brass) of G.M. hydrants valves,  



branch pipe nozzle etc. at least once in a month.




(ad)
Maintenance / operation of fire pumps at least once in a       



month min 15 minutes (in Manual auto mode).




(ae)
Cleaning of all hydrant boxes etc. 




(af)
Providing gland packing and washers etc.

3.
Earnest Money Deposit (EMD)

(a)
The Govt. Department, Public Sector Units, Small Scale Industrial (SSI) Units, 

(Only permanently registered) and agencies registered with NSIC etc, are 

exempted from submitting EMD.


(b)
SSI Units and agencies requesting for exemption from submission of EMD 

shall submit a copy of their Registration Certificate. Only such Units and         

agencies registered for the same trade/item for which the tender is relevant 

shall be exempted from submission of EMD.


(c)
EMDs of unsuccessful tenders shall be refunded within reasonable time     

without interest.


(d)
The tenders without EMD or partial EMD shall be summarily rejected.
-9-

(e)
Earnest money to successful tenderer shall be returned after submitting the 

Initial Security Deposit (ISD) @ 10% of contract value in the form as           

prescribed under General Financial Rules 2005.   No interest will accrue on 

such deposit.

(f)
IN  THE EVENT  OF  THE  TENDER  BEING   ACCEPTED.   In the event of 

acceptance of Tender, the Agency/firm shall be at liberty either to accumulate 

the  EMD towards 10% S.D. amount or can receive the EMD after deposit of 

S.D. as per condition of contract.
4.
Security Deposit.  The agency shall have to deposit @ 10% of the contract value as 
security before start of the work.  The same shall be retained till the contract is in force 
and shall be returned after getting clearance from the Engineer-in-Charge after 
expiry of the contract.
5.
Commencement of Work.   The agency shall be bound to take over the 
system with 
complete  installations  within a period of 07 days from the issue of the work order  
failing which EMD is liable to be forfeited.

6.
Rate Quoted.   


(a)
The rate shall be inclusive of all materials (as per schedule of  requirement) 
     
labours, T&P, Taxes, Duties, over heads and profits etc and everything      

necessary for 
carrying the work as specified in the tender or as directed.


(b)
The rates quoted by the contractors will be FIRM throughout the currency of 

contract including extension of time, if granted and shall not be subject to any 

fluctuation due to variation in cost of material and labour etc.


(c)
Rates quoted by contractor shall include removing, shifting, reinstalling       

restoring of the furniture and equipment etc of the premises to get the work 

done.
7.
Compliance of Labour Laws and Insurance.  


(a)
The contractor shall at his 
expenses, ensure due compliance with all 

applicable and governing labour 
laws, rules, regulations and bye-laws 

of contract and State/Central Govt. regulations and other local            

authorities and further to defend indemnify and keep the owner         

(Principal Employer) harmless for any liability or penalty which may be 

imposed by State/Central Govt. and / or other local authorities.  Also 

from all claims, suits or proceedings that may be brought against the 

owner arising under, growing brought by an employee of the contractor, 

by  third  party by State/Central Govt. and’ or; local authorities.  The 

contractor  shall  ensure  due  compliance  with  all provisions of the 

following Acts and liabilities :- 


(i)
Minimum Wages Act.



(ii)
Payment of Wages Act.

(iii) Contract Labour (regulation & Abolition) Act.







-10-



(iv)
Employees State Insurance, Workmen Compensation and      


employees Liability Insurance any other insurance required     


under law or regulation or by owner.



(v)
Accidental injury to workmen and damage to property or to any 


person or third party.



(vi)      Payment of Bonus.


(b)
The contractor shall indemnify and keep the owner/Principal employer 

harmless of all claims, damages or compensation payable by law in 

respect or in consequence of any accident or damage arising under or 

by reason of this agreement or execution of contract.


(c)
The work shall comply with the latest Local Authorities regulations and 

shall be carried out to the entire satisfaction of CBSE, it shall be        

responsibility of the contractor to obtain prior approval of Local          

Authorities/Bodies, if any at his cost.  In case of any dispute decision 

of the Tender Inviting Authority shall be final and binding on the         

contractor.

8.
Printed Conditions. Any conditions on letterhead or otherwise will not be 
considered and contract will be governed solely on the conditions of contract 
stipulated herein.

9.
Accommodation. The contractor shall be required to make his own 
arrangement of accommodation for his worker/staff and storage of materials.

10.
If on checking there are differences between the rates given by the contractor 
in word and figure or in the amount worked by him, the following procedure 
shall be followed :-


(a)
When there is difference between the rates in figure and in words, the 

rates, which correspond to the amounts worked out by the contractor, 

shall be taken as correct.


(b)
When the amount of an item is not worked by the contractor or it do not 

correspond with the rate written either in figures or on words, then the 

rate quoted by the contractor in words shall be taken as correct.


(c)
When the rates quoted by the contractor in figures and in words tallies 

but the amount is not worked out correctly, the rate quoted by the     

contractor shall be taken as correct and not the amount.

11.
Extension of Contract.   The contract shall be valid for a period of one year at initial 
instance (It can be extended further on mutually agreed rates and terms and 
conditions for another one year or yearly basis).

12.
Termination of Contract. The contract can be terminated by giving advance 
notice for two calendar months in writing.
-11-
13.
Experience.  The tenderers should have adequate experience (minimum  three 
years) in maintaining and manning of these installations and submit a proof 
thereof along with tender.  In case their experience is found inadequate the Board 
reserves right to reject the tender (s).

14.
Local Regulations. The contractor shall ensure that operation and maintenance of 
installation is done as per the rules and regulations of Chief Fire Officer, of fire 
service. The contractor shall also abide by the requirements of our office and shall 
strictly follow the instructions from time to time.
15.
Log Book.


(a)
The contractor shall maintain a log book at the site wherein entries like       

general conditions, fortnightly/periodical duties/maintenance carried out and 

results 
achieved shall be recorded.  This drill shall apply for all equipments/ 

components.  
The specimen of log-book shall be got approved.  The entries 

in log-book shall be got signed by Assistant Secretary (Admn) or by him.


(b)
In case of any actuation of fire detectors for testing/actual fire/false alarm, the 

contractor shall inform the Engineer-in-Charge.  The contractor shall also   

inform the Engineer-in-Charge in case of any abnormal functioning in any   

system and make necessary entries in the log book.

16.
Tools and Plants. The contractor shall provide necessary tools and plants required 
for carrying out the maintenance work.
(a) The pump sets if required any repairs, the parts (impellar, Bush, sleeve, coupling etc.
17.
Behaviour of Staff.   The personnel deputed for maintenance work shall behave                                                                   
properly with Board staff and public.  They shall behave politely and shall maintain 
discipline.
(a) The manpower/personnel deployed must be trustworthy and committed. The antecedent of the manpower must be got properly verified through the Police.
18.
Arbitration.  In case of any dispute between the parties arising out or in relation to 
the agreement,  the dispute shall be reflected to a sole arbitrator to be appointed by 
the Board   and decision of such arbitration shall be inclusive and 
binding on both the 
parties.  The Arbitration Act 1940 and subsequent amendments their in shall be 
applicable.

19.
Payment Terms. Payment  shall be made on monthly basis after making 
deduction of 
Income tax/any other tax as per Govt. rules.

20.
Identification. All the equipments like fire hydrants, valves, hose reel, fire 
detector panel, etc. shall be serially numbered for proper / easy identification.

-12-
21.
Coordination with other Agencies.  The contractor shall extend all cooperation  
to the other agencies in r/o work in the Board premises for any purpose.

22.
Penalties and ID.   In case maintenance work has not been attended to/defect has 
not been set right, the penalty shall be imposed as per following :-

	Sl. No.
	Description
	Penalty

(In Rs)

	1.
	If main control panel is not set right within 24 hrs
	400/- day

	2.
	If any of the Zone remains out of order for more than 24 hrs
	150/- day

	3.
	If PA system is out of order for more than 24 hrs
	150/- day

	4.
	If any circuit is faulty for more than 24 hrs
	50/- day

	5.
	If battery charging unit is out of order for more than 24 hrs
	100/- day

	6.
	If fire pump panel etc. are under breakdown for more than 24 hrs
	500/- day

	7.
	If valves are leaking/pressure switches/air vessel etc. are not working
	150/- day

	8.
	If routine / periodical maintenance is not carried out 
	1% per week



Note  :  While imposing the above penalty/ID, due consideration shall be given to 

   the time required for carrying out the necessary repairs.
23.
Contractor will inspect entire installation before quoting their rates.  If any 
alteration to 
improve the system needs to be undertaken same shall be intimated in detail item wise 
with complete specification alongwith item-wise estimate rate.  This proposal shall be 
given on the letter head of contractor which shall be kept in separate envelope.

24.
Performance of contractor shall be observed for first three month. If performance  
of the contractor in first three month is not found to be satisfactory, the contract shall be 
terminated by serving notice for one week.

25.
Contractor will provide name and detail of their personal, looking after the 
maintenance 
of above installation.  Contractor will have to obtain approval for the workmen being 
deputed at above sites and bio-data shall be submitted accordingly.  Person who have 
not been authorized by this office shall not be deputed on the job.  
26.
The agency will have to provide staff for 24 hrs Operation and Maintenance of Fire 
System. The additional staff if required for regular maintenance, servicing and 
attending to fault shall have to be arranged by the agency within the quoted rates.  
The agency shall have to engage experienced and skilled staff.
-13-
27.
The agency shall take all precautionary measures for safety of his workers 
during performance of the duties.
28.
The staff  to be engaged should possess qualification as given below :-

(a) Fire Fighting Operator -  03 Nos (Holding five years experience in the                  relevant field having fire fighting certificate from the Competent/Designated Authority)*.

29.
The agency shall provide uniform for the staff on duty.

30.
A minimum pressure of 3.5 Kg./CM2   has to be maintained in the system.

31.
Piping system shall be checked and reported to the Engineer-in-Charge.

32.
Components such as switch gear shall be supplied by the Board to the agency.

33.
Distilled water, cleaning materials, CTC, COTTON, Old Dhoti, Pilot Lamps, Gland 
Dori, 
grease, packing sheets, nut & bolts, HRC fuses, tourch and other materials 
including the control spares shall be provided by the agency.

34.
Dismantled material shall be returned to the Board.

35.
The agency shall maintain a line diagram of the system in the Pump House/ 
Control Room.

36.
The watch and ward of the complete installation including the Pump House and Fire 
Hydrants inside and outside the building shall be the responsibility of the agency.

37.
Operators presence all the time is the essentiality of the contractor, hence 
operator must be on duty and plant room should not be left unattended.  In case the 
reliever does not report,  the first operator shall continue to be on duty.
38.
The agency shall arrange to give ‘Live Demo’ of the complete system on  
monthly basis as decided by the Competent Authority and six monthly basis in 
presence of the Fire Authorities.

39.
After expiry of the contract period, contractor shall hand over entire installation with all 
complete equipments in good working condition as detailed in Schedule of Work.  
Final bill (last two month) shall be settled only after 
handing over of above installation 
in good working/operational condition.  If system is found un-operational or the system 
appears poorly maintained with low efficiency the cost for making the system 
operational; shall be recovered from the pending dues to the contractor. 
-14-
     (Signature of the Tenderer)​​​​​​​​​​​​​​​​​​​​​​​​​____________________
   Name & Address of Tenderers with seal____________________
ENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE

35-B, CIVIL STATION, M.G. MARG, CIVIL LINES

ALLAHABAD

MAINTENANCE AND OPERATION OF WET RISER, SPRINKLER SYSTEM
A. Daily Check.


1.
Checking of all floor hydrant valves, hose pipes, hose reel, nozzles, 

hose reel drums pumps, hydrants etc.


2.
Checking of sprinkler line pressure and sprinkler head.


3.
Checking of valves and N.R.V.
 4.
Checking of hydrant pressure and recording in log book.

 5.
Checking of water and diesel level of engine and topping up with the 

fuel.
     B.
Monthly Check.


1.
Testing of automatic working of fire hydrant system.


2.
Testing of automatic working of sprinkler system.


3.
Checking and cleaning of all starter contracts of electric panels.


4.
Checking and testing of automatic pressure switches of pumps.


5.
Cleaning of alarm gong and its drain valve connection.


6.
Conducting drill for the system.
     C.
Quarterly Check.


1.
Checking of performance of electric panels (Voltage & Current load).


2.
Checking of wiring, cable termination glands.

3.
Checking of fuses and bulbs.


4.
Checking of glands of sluice valves.


5.
Cleaning of cooling water system of the engine.


6.
Checking of battery charging.  To be charged if required and checking 

of gravity of acid.

-15-
       D.
Half Yearly Check.


1.
Replacement of greases.


2.
Changing of glands of pumps.


3.
Checking of alignments and foundation bolts adjustment of Pumps.


4.
Checking of working of NRV pressure plate.


5.
Checking of all hydrant and sprinkler line from leakage angle.

6.
To check, clean and adjust the relays switches etc..

7.
Oiling and greasing of all hydrants sluice valve N.R.V. etc.


8.
Testing of fire hose at required pressure.


9.
Testing hose reels and band pipes at required pressure.


10.
Servicing of fire pumps as manufacturer’s manual through authorised 

dealer.


11.      To check the working of the air release value.


12.      Checking of the oil pressure in the Diesel Engine & condition of the 


engine oil.
Signature of the Tenderer_ _ _ _ _ _ _ _ _ _ _ _ _ _ _
   Name & Address of Tenderers with seal_ _ _ _ _ _ __
_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _

-16-
LIST OF INSTALLATION

	Sl. No.
	Details of Electrical & Mechanical Installations


	Quantity

	A.
	24 hrs Operation and Maintenance of Fire Fighting System consisting of wet riser and sprinkler system including the installation mentioned as under alongwith the control panel.


	

	1.
	Electric driven main fire pump set of 75 HP 


	01 Nos

	2.
	Diesel engine driven main fire pump set with auto starting panel of 79 HP


	01 Nos

	3.
	Electric driven pressurization pump 15 HP


	01 Nos

	4.
	Electric driven terrace pump having 30 mtrs discharge head of 12.5 HP


	01 Nos

	5.
	Mono block self priming drainage pump of 90 LMP discharge of 10 mtrs


	01 Nos

	6.
	Double Headed internal valve


	18 Nos

	7.
	Single Headed external hydrant


	06 Nos

	8.
	Quartzoid bulb type sprinkler


	40 Nos

	9.
	Booster pump 15 HP


	02 Nos

	10.
	De-watering pump set 2 HP


	02 Nos

	11.
	Water supply cubical panel board


	01 Nos

	B.
	Operation and Maintenance of Fire Alarm system comprising of installations mentioned as under :-


	

	1.
	Sensor type detector system


	94 Nos


-17-
	2.
	Sensor type smoke detector system


	93 Nos

	3.
	Manual Call Box 


	24 Nos

	4.
	Two zone sector panel


	08 Nos

	C.
	Main Control Panel Consisting of :-


	

	1.
	Ten one sector panel


	

	2.
	Talk back master starter


	01 set

	3.
	Announcement control desk


	01 set

	4.
	100 W Amplifier with all accessories


	02 set

	5.
	Monitor panel for Loudspeaker with volume control


	01 Nos

	6.
	Goose neck microphone with stand


	01 set


-18-
CENTRAL BOARD OF SECONDARY EDUCATION

REGIONAL OFFICE BUILDING

35-B, CIVIL STATION, CIVIL LINES, M. G. MARG, ALLAHABAD-211001

Last date for receipt of tender :26 March 2012 upto 01.00 p.m.
PART II : PRICE BID

(Schedule of Quantity)
Name of Work :  24 hrs Operation and Maintenance of Fire Fighting System 

      
       consisting of wet riser and sprinkler system including the      

                             installation mentioned as under alongwith the control panel.
	Sl. No.
	Description of items
	Rate per month including of all taxes



	     A.
	24 hrs Operation and Maintenance of Fire Fighting System consisting of wet riser and sprinkler system including the installation mentioned as under alongwith the control panel.


	

	1.
	Electric driven main fire pump set of 75 HP – 01 Nos.


	

	2.
	Diesel engine driven main fire pump set with auto starting panel of 79 HP – 01 Nos.

s
	

	3.
	Electric driven pressurization pump 15 HP – 01 Nos.


	

	4.
	Electric driven terrace pump having 30 mtrs discharge head of 12.5 HP – 01 Nos.


	

	5.
	Mono block self priming drainage pump of    90 LMP discharge of 10 mtr – 01 Nos


	

	6.
	Double Headed internal valve – 18 Nos


	

	7.
	Single Headed external hydrant – 06 Nos


	

	8.
	Quartzoid bulb type sprinkler – 40 Nos


	

	9.
	Booster pump 15 HP – 02 Nos


	

	10.
	De-watering pump set 2 HP – 02 Nos


	

	11.
	Water supply cubical panel board – 01 Nos


	


-19-
	    B.
	Operation and Maintenance of Fire Alarm system comprising of installations mentioned as under :-


	

	1.
	Sensor type detector system – 94 Nos


	

	2.
	Sensor type smoke detector system – 93 Nos


	

	3.
	Manual Call Box – 24 Nos


	

	4.
	Two zone sector panel – 08 Nos


	

	     C.
	Main Control Panel Consisting of :-


	

	1.
	Ten one sector panel


	

	2.
	Talk back master starter – 01 Set


	

	3.
	Announcement control desk – 01 Set


	

	4.
	100 W Amplifier with all accessories – 02 Set


	

	5.
	Monitor panel for Loudspeaker with volume control – 01 Nos


	

	6.
	Goose neck microphone with stand – 01 Set


	


     Signature of the Tenderer_ _ _ _ _ _ _ _ _ _ _ _ _ _ _
   Name & Address of Tenderers with seal_ _ _ _ _ _ __
_ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _

Telephone/Mobile No. _ _ _ _ _ _ _ 

Place : _ _ _ _ _ _ _ _ _ _ _ _ _ _ _ _
